新冷站项目目标 Mac Codex 一键安装部署手册

适用于另一台全新 Mac 本地平台；可联网安装；目标是让目标主机 Codex 直接照文档执行。

版本日期：2026-06-18    默认边界：READ_ONLY_MODE=1 + shadow    系统范围：冷站优先

关键结论 这份文档可以直接交给目标 Mac 上的 Codex：先粘贴第 2 章提示词，再让目标 Codex 写入并执行第 3 章脚本。脚本默认只部署本地平台和 mock PLC Gateway，不会真实写 PLC；真实闭环必须额外打开双重确认并完成现场联锁、回读、回退验收。

# 1. 使用方式

在目标 Mac 打开 Codex，新建一个线程。

把第 2 章“直接喂给目标主机 Codex 的提示词”全文粘贴进去。

把真实仓库地址替换到 REPO_URL；没有真实 PLC 网关时保持 PLC_GATEWAY_MODE=mock。

让目标 Codex 执行脚本并返回 healthz、URL、合同检查和日志摘要。

只有现场点表、写入白名单、PLC 联锁、回读和回退验收完成后，才允许讨论 ENABLE_REAL_PLC_WRITE=1。

| 目标机部署基线 |  |
| --- | --- |
| 目标系统 | 另一台 Mac；可联网；用 Homebrew 安装 git、node@22、nginx。 |
| 部署目录 | $HOME/Documents/智慧冷冻站，脚本会把仓库中的旧绝对路径替换为目标机路径。 |
| 运行端口 | 前台 3001，管理端 3002，BFF 8787，PLC Gateway 8877。 |
| 默认边界 | READ_ONLY_MODE=1，towerApproachDispatchMode=shadow，mock Gateway 不做真实 PLC 写入。 |
| 适用系统 | 冷站优先：冷机、冷冻泵、冷却泵、冷却塔、COP、AI 优化建议、执行单治理。 |

# 2. 直接喂给目标主机 Codex 的提示词

将下面整段粘贴给目标 Mac 上的新 Codex 线程。目标 Codex 不需要知道当前电脑路径，只需要替换 REPO_URL。

Codex 提示词

你现在在一台全新的目标 Mac 上，不是在原开发电脑。请按以下要求完成“智慧冷冻站新项目本地平台一键安装”。 目标： 1. 在目标 Mac 部署 BFF、前台 Shell、管理端和 PLC Gateway mock。 2. 默认只启用 read-only + shadow，不允许真实 PLC 写入。 3. 安装完成后输出 URL、healthz 结果、关键日志路径和验收结论。 必须使用的变量： REPO_URL=<替换成真实 git 仓库地址> SITE_ID=new_chiller_site_001 SITE_NAME=新冷站项目 DEPLOY_DIR=$HOME/Documents/智慧冷冻站 PLC_GATEWAY_MODE=mock ENABLE_REAL_PLC_WRITE=0 执行要求： 1. 先检查目标机系统、Node、npm、brew、端口占用。 2. 在 /tmp/install_chiller_target_mac.sh 写入本文档“完整一键安装脚本”。 3. 执行： REPO_URL="$REPO_URL" SITE_ID="$SITE_ID" SITE_NAME="$SITE_NAME" DEPLOY_DIR="$DEPLOY_DIR" bash /tmp/install_chiller_target_mac.sh 4. 若脚本失败，不要改安全边界；先读 /tmp/chiller-*.log 和终端报错，修复路径、端口、依赖或仓库问题。 5. 最终回报必须包含： - 前台 URL 是否 2xx - 管理端 URL 是否 2xx - BFF /healthz JSON 摘要 - PLC Gateway /healthz JSON 摘要 - npm --prefix apps/chiller-bff run check:contract 是否通过 - 是否仍处于 READ_ONLY_MODE=1 和 shadow - 未完成项：真实 PLC 点表、写入白名单、回读、联锁、回退验收 安全边界： - 不要把 mock PLC Gateway 当成真实 PLC。 - 不要把安装成功等同于真实闭环成功。 - 未经现场书面确认，不得设置 ENABLE_REAL_PLC_WRITE=1。 - pump-delta-t 不进入无人值守 enforced；冷却塔接近度也必须经过 PLC 本地保护、回读和回退验收。

# 3. 完整一键安装脚本

目标 Codex 应把本节脚本写入 /tmp/install_chiller_target_mac.sh 后执行。脚本包含依赖安装、克隆仓库、路径修正、npm ci、项目初始化、mock PLC Gateway、BFF/前台/管理端启动和基础验收。

install_chiller_target_mac.sh

#!/usr/bin/env bash set -euo pipefail # ===== 必填/可改变量 ===== # 目标 Codex 执行前必须把 REPO_URL 换成真实仓库地址。 REPO_URL="${REPO_URL:-}" DEPLOY_DIR="${DEPLOY_DIR:-$HOME/Documents/智慧冷冻站}" SITE_ID="${SITE_ID:-new_chiller_site_001}" SITE_NAME="${SITE_NAME:-新冷站项目}" # 默认安全模式：只读 + shadow，不真实写 PLC。 BFF_PORT="${BFF_PORT:-8787}" FRONTEND_PORT="${FRONTEND_PORT:-3001}" ADMIN_PORT="${ADMIN_PORT:-3002}" PLC_GATEWAY_PORT="${PLC_GATEWAY_PORT:-8877}" APP_MODE="${APP_MODE:-site-local}" APP_MODE_LABEL="${APP_MODE_LABEL:-现场本地联调}" READ_ONLY_MODE="${READ_ONLY_MODE:-1}" PLC_GATEWAY_MODE="${PLC_GATEWAY_MODE:-mock}" # mock ¦ real ¦ none ENABLE_REAL_PLC_WRITE="${ENABLE_REAL_PLC_WRITE:-0}" I_UNDERSTAND_REAL_PLC_WRITE="${I_UNDERSTAND_REAL_PLC_WRITE:-NO}" LEGACY_BASE_URL="${LEGACY_BASE_URL:-https://www.ssge.com.cn:8098}" REALTIME_PARAMS_BASE_URL="${REALTIME_PARAMS_BASE_URL:-https://ln.szgreenenergy.com}" REALTIME_PARAMS_TIMEOUT_MS="${REALTIME_PARAMS_TIMEOUT_MS:-1500}" MIN_CONDENSER_INLET_TEMP_C="${MIN_CONDENSER_INLET_TEMP_C:-22}" ADMIN_DB_FILE="${ADMIN_DB_FILE:-$DEPLOY_DIR/apps/chiller-bff/.local/admin.sqlite}" say() { printf '\n[%s] %s\n' "$(date '+%H:%M:%S')" "$*"; } fail() { printf '\n[FAIL] %s\n' "$*" >&2; exit 1; } warn() { printf '\n[WARN] %s\n' "$*" >&2; } if [ -z "$REPO_URL" ]; then fail "REPO_URL 未设置。示例：REPO_URL=https://github.com/org/repo.git bash install_chiller_target_mac.sh" fi say "1/9 检查并准备 Homebrew / Git / Node 22 / nginx" if ! command -v brew >/dev/null 2>&1; then say "Homebrew 未安装，开始安装。若目标机策略禁止自动安装，请先人工安装后重跑。" NONINTERACTIVE=1 /bin/bash -c "$(curl -fsSL https://raw.githubusercontent.com/Homebrew/install/HEAD/install.sh)" fi if [ -x /opt/homebrew/bin/brew ]; then eval "$(/opt/homebrew/bin/brew shellenv)" elif [ -x /usr/local/bin/brew ]; then eval "$(/usr/local/bin/brew shellenv)" fi brew list git >/dev/null 2>&1 ¦¦ brew install git brew list node@22 >/dev/null 2>&1 ¦¦ brew install node@22 brew list nginx >/dev/null 2>&1 ¦¦ brew install nginx export PATH="$(brew --prefix node@22)/bin:$PATH" node_major="$(node -p 'Number(process.versions.node.split(".")[0])')" [ "$node_major" -ge 22 ] ¦¦ fail "Node 版本不足：$(node -v)，需要 22.x 或更高。" say "2/9 获取或更新代码：$DEPLOY_DIR" mkdir -p "$(dirname "$DEPLOY_DIR")" if [ -d "$DEPLOY_DIR/.git" ]; then git -C "$DEPLOY_DIR" fetch --all --prune git -C "$DEPLOY_DIR" pull --ff-only ¦¦ warn "git pull 失败，保留当前代码继续尝试。" else git clone "$REPO_URL" "$DEPLOY_DIR" fi cd "$DEPLOY_DIR" say "3/9 修正目标机部署路径" export DEPLOY_DIR find scripts -maxdepth 1 -type f -name "*.sh" -print0 \ ¦ xargs -0 perl -0pi -e 's#/Users/billchow/Documents/智慧冷冻站#$ENV{DEPLOY_DIR}#g' chmod +x scripts/*.sh ¦¦ true say "4/9 安装前端和 BFF 依赖" npm --prefix apps/chiller-bff ci npm --prefix apps/chiller-shell-v1 ci npm --prefix apps/chiller-admin-v1 ci say "5/9 写入目标机本地环境文件" cat > apps/chiller-shell-v1/.env.local <<EOF VITE_BFF_BASE_URL=http://127.0.0.1:${BFF_PORT} VITE_LEGACY_BASE_URL=${LEGACY_BASE_URL} VITE_SITE_ID=${SITE_ID} VITE_TREND_RANGE=24h VITE_APP_MODE=${APP_MODE} VITE_APP_MODE_LABEL=${APP_MODE_LABEL} VITE_APP_READ_ONLY=${READ_ONLY_MODE} VITE_UI_BADGE_STATE_URL=/ui-badge-state-v1.8.json EOF cat > apps/chiller-admin-v1/.env.local <<EOF VITE_ADMIN_API_BASE_URL=http://127.0.0.1:${BFF_PORT} VITE_LEGACY_BASE_URL=${LEGACY_BASE_URL} VITE_ADMIN_APP_MODE=${APP_MODE} VITE_ADMIN_APP_MODE_LABEL=${APP_MODE_LABEL} VITE_ADMIN_READ_ONLY=${READ_ONLY_MODE} VITE_ADMIN_USE_MOCKS=false VITE_ADMIN_DEV_LOGIN=true VITE_ADMIN_DEFAULT_SITE_ID=${SITE_ID} VITE_ADMIN_BOOTSTRAP_USERNAMES=admin EOF say "6/9 初始化新项目配置库" mkdir -p "$(dirname "$ADMIN_DB_FILE")" ADMIN_DB_FILE="$ADMIN_DB_FILE" SITE_ID="$SITE_ID" \ node apps/chiller-bff/scripts/ensure-energy-demo-subsystems.js \ --profile=b25-cold-only \ --site-id="$SITE_ID" ADMIN_DB_FILE="$ADMIN_DB_FILE" SITE_ID="$SITE_ID" SITE_NAME="$SITE_NAME" \ npm --prefix apps/chiller-bff run admin:ensure-runtime-config -- \ --site-id="$SITE_ID" \ --site-name="$SITE_NAME" \ --min-condenser-inlet-temp-c="$MIN_CONDENSER_INLET_TEMP_C" \ --tower-approach-dispatch-mode=shadow say "7/9 准备 PLC Gateway" if [ "$PLC_GATEWAY_MODE" = "mock" ]; then mkdir -p .local cat > .local/plc-gateway-mock.mjs <<'NODE' import http from "node:http"; const port = Number(process.env.PLC_GATEWAY_PORT ¦¦ 8877); function json(res, status, body) { res.writeHead(status, {"content-type": "application/json"}); res.end(JSON.stringify(body)); } const server = http.createServer((req, res) => { if (req.method === "GET" && req.url === "/healthz") { json(res, 200, {ok: true, mode: "mock", plcWrite: false}); return; } if (req.method === "POST" && (req.url === "/plc/dispatch/tower-approach" ¦¦ req.url === "/plc/rollback/tower-approach")) { let raw = ""; req.on("data", (chunk) => { raw += chunk; }); req.on("end", () => { const payload = raw ? JSON.parse(raw) : {}; const command = payload.command ¦¦ {}; json(res, 200, { ok: true, accepted: true, mode: "mock", plcWrite: false, writtenPoint: req.url.includes("rollback") ? "TCWS_SP_ROLLBACK" : "TCWS_SP", writtenValue: command.targetTcwsC ?? command.rollbackTarget?.targetTcwsC ?? null, readbackValue: command.targetTcwsC ?? command.rollbackTarget?.targetTcwsC ?? null, plcMode: "simulated-auto", interlockOk: true, alarmBlocked: false }); }); return; } json(res, 404, {ok: false, error: "not_found"}); }); server.listen(port, "127.0.0.1", () => console.log(`mock PLC gateway on ${port}`)); NODE launchctl remove "com.chiller.plc-gateway.mock.${PLC_GATEWAY_PORT}" >/dev/null 2>&1 ¦¦ true : > "/tmp/chiller-plc-gateway-${PLC_GATEWAY_PORT}.log" launchctl submit \ -l "com.chiller.plc-gateway.mock.${PLC_GATEWAY_PORT}" \ -o "/tmp/chiller-plc-gateway-${PLC_GATEWAY_PORT}.log" \ -e "/tmp/chiller-plc-gateway-${PLC_GATEWAY_PORT}.log" \ -- /bin/zsh -lc "cd \"$DEPLOY_DIR\" && export PLC_GATEWAY_PORT=\"$PLC_GATEWAY_PORT\" PATH=\"$(brew --prefix node@22)/bin:\$PATH\" && exec node .local/plc-gateway-mock.mjs" elif [ "$PLC_GATEWAY_MODE" = "real" ]; then curl -fsS "http://127.0.0.1:${PLC_GATEWAY_PORT}/healthz" >/tmp/chiller-plc-health.json \ ¦¦ fail "真实 PLC Gateway 未就绪：http://127.0.0.1:${PLC_GATEWAY_PORT}/healthz" else warn "PLC_GATEWAY_MODE=$PLC_GATEWAY_MODE，跳过 Gateway 启动。" fi say "8/9 启动 BFF + 前台 + 管理端" APP_MODE="$APP_MODE" BFF_PORT="$BFF_PORT" FRONTEND_PORT="$FRONTEND_PORT" \ "$DEPLOY_DIR/scripts/stop_local_stack.sh" ¦¦ true APP_MODE="$APP_MODE" APP_MODE_LABEL="$APP_MODE_LABEL" READ_ONLY_MODE="$READ_ONLY_MODE" \ BFF_PORT="$BFF_PORT" FRONTEND_PORT="$FRONTEND_PORT" SITE_ID="$SITE_ID" \ LEGACY_BASE_URL="$LEGACY_BASE_URL" REALTIME_PARAMS_BASE_URL="$REALTIME_PARAMS_BASE_URL" \ REALTIME_PARAMS_TIMEOUT_MS="$REALTIME_PARAMS_TIMEOUT_MS" \ "$DEPLOY_DIR/scripts/start_local_stack.sh" launchctl remove "com.chiller.admin.${APP_MODE}.${ADMIN_PORT}" >/dev/null 2>&1 ¦¦ true : > "/tmp/chiller-admin-${APP_MODE}-${ADMIN_PORT}.log" launchctl submit \ -l "com.chiller.admin.${APP_MODE}.${ADMIN_PORT}" \ -o "/tmp/chiller-admin-${APP_MODE}-${ADMIN_PORT}.log" \ -e "/tmp/chiller-admin-${APP_MODE}-${ADMIN_PORT}.log" \ -- /bin/zsh -lc "cd \"$DEPLOY_DIR/apps/chiller-admin-v1\" && export PATH=\"$(brew --prefix node@22)/bin:\$PATH\" VITE_ADMIN_API_BASE_URL=\"http://127.0.0.1:${BFF_PORT}\" VITE_ADMIN_USE_MOCKS=false VITE_ADMIN_DEV_LOGIN=true VITE_ADMIN_DEFAULT_SITE_ID=\"$SITE_ID\" && exec npm run dev -- --host 127.0.0.1 --port \"$ADMIN_PORT\"" wait_http() { local name="$1"; local url="$2"; local i for i in $(seq 1 30); do if curl -fsS "$url" >/dev/null 2>&1; then printf '[OK] %s: %s\n' "$name" "$url" return 0 fi sleep 1 done return 1 } wait_http "BFF" "http://127.0.0.1:${BFF_PORT}/healthz" ¦¦ fail "BFF 未就绪" wait_http "前台" "http://127.0.0.1:${FRONTEND_PORT}/" ¦¦ fail "前台未就绪" wait_http "管理端" "http://127.0.0.1:${ADMIN_PORT}/" ¦¦ fail "管理端未就绪" if [ "$PLC_GATEWAY_MODE" != "none" ]; then wait_http "PLC Gateway" "http://127.0.0.1:${PLC_GATEWAY_PORT}/healthz" ¦¦ fail "PLC Gateway 未就绪" fi say "9/9 验收检查" npm --prefix apps/chiller-bff run check:contract set +e SITE_ID="$SITE_ID" BFF_BASE_URL="http://127.0.0.1:${BFF_PORT}" FRONTEND_BASE_URL="http://127.0.0.1:${FRONTEND_PORT}" \ "$DEPLOY_DIR/scripts/check_stack.sh" "$SITE_ID" stack_rc=$? set -e if [ "$stack_rc" -ne 0 ]; then warn "check_stack 返回非零，通常是旧系统/现场上游未通。安装是否成功以 BFF/前台/管理端 health 为准。" fi if [ "$ENABLE_REAL_PLC_WRITE" = "1" ]; then if [ "$I_UNDERSTAND_REAL_PLC_WRITE" != "YES" ]; then fail "禁止打开真实写入：必须同时设置 ENABLE_REAL_PLC_WRITE=1 和 I_UNDERSTAND_REAL_PLC_WRITE=YES。" fi curl -fsS "http://127.0.0.1:${PLC_GATEWAY_PORT}/healthz" >/dev/null ADMIN_DB_FILE="$ADMIN_DB_FILE" SITE_ID="$SITE_ID" \ npm --prefix apps/chiller-bff run admin:ensure-runtime-config -- \ --site-id="$SITE_ID" \ --tower-approach-dispatch-mode=enforced \ --tower-approach-dispatch-approve-endpoint="http://127.0.0.1:${PLC_GATEWAY_PORT}/plc/dispatch/tower-approach" \ --tower-approach-dispatch-rollback-endpoint="http://127.0.0.1:${PLC_GATEWAY_PORT}/plc/rollback/tower-approach" \ --tower-approach-dispatch-timeout-ms=8000 warn "已切 tower approach enforced 配置。仍需现场完成点位签字、PLC 联锁、回读和回退验收后才能真实运行。" fi cat <<EOF === 安装完成 === 前台: http://127.0.0.1:${FRONTEND_PORT} 管理端: http://127.0.0.1:${ADMIN_PORT} BFF: http://127.0.0.1:${BFF_PORT}/healthz PLC网关: http://127.0.0.1:${PLC_GATEWAY_PORT}/healthz 项目: ${SITE_ID} / ${SITE_NAME} 配置库: ${ADMIN_DB_FILE} 默认边界: READ_ONLY_MODE=${READ_ONLY_MODE}, PLC_GATEWAY_MODE=${PLC_GATEWAY_MODE} 日志: /tmp/chiller-*.log EOF

# 4. 部署架构

| 层级 | 端口 | 职责 | 验收信号 |
| --- | --- | --- | --- |
| 前台 Shell | 3001 | 运行端页面、总览、趋势、优化演示、执行单审阅。 | HTTP 2xx；/optimize-demo?siteId=... 可打开。 |
| BFF | 8787 | 聚合站点数据、AI Advisor、执行单、管理端 API、合同检查。 | /healthz 返回 ok，check:contract 通过。 |
| 管理端 | 3002 | 站点配置、子系统能力、runtime-config、点位映射复核。 | VITE_ADMIN_USE_MOCKS=false 下可进入登录/配置页。 |
| PLC Gateway | 8877 | HTTP 到 PLC 协议的隔离层；mock 模式仅模拟回读。 | /healthz 返回 mode=mock 或 real。 |
| PLC / SCADA | 现场网络 | 真实点位、联锁、手自动、回读、回退。 | 现场签字后才允许真实写入。 |

# 5. 安装变量说明

| 变量 | 默认值 | 是否必改 | 说明 |
| --- | --- | --- | --- |
| REPO_URL | 空 | 是 | 真实 git 仓库地址；脚本为空会停止。 |
| DEPLOY_DIR | $HOME/Documents/智慧冷冻站 | 建议确认 | 目标机部署目录。 |
| SITE_ID | new_chiller_site_001 | 建议改 | 目标项目唯一站点 ID。 |
| SITE_NAME | 新冷站项目 | 建议改 | 管理端展示名称。 |
| PLC_GATEWAY_MODE | mock | 否 | mock / real / none；默认不会真实写 PLC。 |
| READ_ONLY_MODE | 1 | 否 | BFF 写保护总闸。 |
| ENABLE_REAL_PLC_WRITE | 0 | 现场前禁止改 | 真实写 PLC 触发变量，必须另配确认短语。 |
| I_UNDERSTAND_REAL_PLC_WRITE | NO | 现场前禁止改 | 只有值为 YES 且 ENABLE_REAL_PLC_WRITE=1 才进入 enforced 配置。 |

# 6. 目标 Codex 执行后的验收标准

| 检查项 | 命令 | 通过标准 |
| --- | --- | --- |
| BFF 健康 | curl http://127.0.0.1:8787/healthz | 返回 JSON；appMode、readOnlyMode、legacyBaseUrl 可读。 |
| 前台入口 | curl -I http://127.0.0.1:3001/ | HTTP 2xx；浏览器可打开。 |
| 管理端入口 | curl -I http://127.0.0.1:3002/ | HTTP 2xx；VITE_ADMIN_USE_MOCKS=false。 |
| PLC Gateway | curl http://127.0.0.1:8877/healthz | mock 模式返回 plcWrite=false；real 模式必须有真实联锁摘要。 |
| 合同检查 | npm --prefix apps/chiller-bff run check:contract | 通过；OpenAPI 示例与 schema 一致。 |
| 本地栈检查 | SITE_ID=$SITE_ID scripts/check_stack.sh $SITE_ID | BFF/前台通过；旧系统上游不通可作为 WARN/现场资源缺口。 |

# 7. 真实 PLC 闭环门禁

禁止误判 安装成功、页面能打开、mock Gateway accepted、BFF ok=true，都不等于真实 PLC 闭环成功。真实闭环的最终真值是：PLC 写入回读、联锁状态、告警闭锁、回退记录和现场签字。

| 门禁 | 冷却塔接近度 | 泵温差修正 |
| --- | --- | --- |
| 第一版策略 | 可做受控 enforced 候选，但默认先 shadow。 | 只做 assisted 小步修正，不做无人值守 enforced。 |
| 写点要求 | AI 专用目标点或明确批准的 TCWS_SP；不得写手自动模式点。 | AI_ChwpFreqTrim_Hz / AI_CwpFreqTrim_Hz，必须是修正量而非 PID 覆盖。 |
| PLC 保护 | 上下限、单步 <=0.5℃、死区、最小保持、告警闭锁、回退。 | 频率上下限、斜率、最小流量、末端安全、回退后闭锁。 |
| 回读验收 | 目标写入值与回读值一致；异常时自动回退或冻结。 | 修正量生效、TTL 到期归零、回退为 0Hz 或稳定值。 |
| 现场资料 | 点位表、权限等级、写风险清单、PLC 逻辑截图/导出。 | 泵频反馈、末端阀位/压差/室温、最小流量保护确认。 |

# 8. 故障处理

| 现象 | 优先检查 | 处理 |
| --- | --- | --- |
| REPO_URL 未设置 | 脚本开头变量 | 补真实 git 地址后重跑。 |
| Node 版本不足 | node -v | brew install node@22，并把 node@22 加入 PATH。 |
| 3001/3002/8787 占用 | lsof -iTCP:<port> -sTCP:LISTEN | 停旧进程或改 FRONTEND_PORT / ADMIN_PORT / BFF_PORT。 |
| BFF 起不来 | /tmp/chiller-bff-*.log | 看 npm、路径、ADMIN_DB_FILE、端口和语法错误。 |
| 前台空白 | /tmp/chiller-shell-*.log 与 VITE_BFF_BASE_URL | 确认 BFF health，确认 .env.local 已写目标端口。 |
| check_stack 失败 | 失败项是 legacy、bff 还是 frontend | legacy 上游不通是现场资源问题；BFF/前台失败才是安装问题。 |
| mock Gateway accepted | /tmp/chiller-plc-gateway-*.log | 只能说明模拟链路通，不代表真实 PLC 写入。 |

# 9. 目标 Codex 最终回报模板

交付回报格式

安装结果： - 部署目录： - Git commit： - SITE_ID / SITE_NAME： - 前台 URL： - 管理端 URL： - BFF /healthz 摘要： - PLC Gateway /healthz 摘要： - check:contract： - check_stack： - 当前安全边界：READ_ONLY_MODE=1/0，towerApproachDispatchMode=shadow/enforced，PLC_GATEWAY_MODE=mock/real - 真实 PLC 写入：未启用 / 已启用（若已启用，必须附现场签字和回读证据） - 日志路径： - 仍缺资源： 1. 真实 PLC 点位表与写入白名单 2. 手自动/联锁/告警闭锁确认 3. 回读一致性与回退测试 4. 30-60 分钟 shadow 对比数据

# 10. 现场交付注意事项

不要让目标 Codex 为了“安装成功”擅自安装 Docker、改系统网络策略或绕过现场安全流程。

点位表只能证明地址和权限，不足以证明 assisted/enforced readiness；必须结合实时趋势、回读、联锁和回退。

冷却塔手自动点属于高风险模式点，默认禁写；优先写 AI 专用目标点或经过批准的目标设定点。

泵温差优化第一版保留人工确认和 PLC 本地保护，不能让 AI 覆盖原 PID 或直接启停泵。

验收口径要分清：安装验收、本地联调验收、shadow 验收、真实 PLC 闭环验收。

# 附录 A. 常用维护命令

# 查看服务端口 lsof -iTCP:3001 -sTCP:LISTEN lsof -iTCP:3002 -sTCP:LISTEN lsof -iTCP:8787 -sTCP:LISTEN lsof -iTCP:8877 -sTCP:LISTEN # 停止本地 BFF + 前台 APP_MODE=site-local BFF_PORT=8787 FRONTEND_PORT=3001 ./scripts/stop_local_stack.sh # 重新启动本地 BFF + 前台 APP_MODE=site-local READ_ONLY_MODE=1 SITE_ID=$SITE_ID BFF_PORT=8787 FRONTEND_PORT=3001 ./scripts/start_local_stack.sh # BFF 合同检查 npm --prefix apps/chiller-bff run check:contract # 查看日志 tail -n 80 /tmp/chiller-bff-*.log tail -n 80 /tmp/chiller-shell-*.log tail -n 80 /tmp/chiller-admin-*.log tail -n 80 /tmp/chiller-plc-gateway-*.log